## Instructions
Clearwell Drawdown Meter Accuracy Test
Name of water treatment plant.
To conduct a clearwell drawdown meter accuracy test follow these steps:
1. Ensure the clearwell is full enough to pump for several minutes without
adding additional water during the test.
2. Turn off wells/raw water pumps and close filters so no water enters the
clearwell.
3. Take a measurement from a fixed point to the top of the water.
4. Read the master meter to the gallon, if possible.
5. Turn on the high service pump and pump for at least five minutes. The
longer you pump, the better the accuracy of the test. Be careful not to
pump the clearwell too low. Turn off the pump.
6. Measure from the same fixed point to the top of the water in the
clearwell. You may need to give the clearwell a few minutes for the level
to stabilize. Subtract the first measurement from the final one.
7. Read the master meter and subtract the previous reading to determine the
total gallons of water metered.
8. Enter clearwell information, the inches the water level dropped and the
gallons metered in the appropriate clearwell worksheet.
Rectangular Clearwell Worksheet
Rectangular Clearwell Example
Rectangular Clearwell Worksheet
Round CW Example
Round CW Worksheet
2 Rectangular Clearwells Worksheet

## Rectangular Clearwell Example
Rectangular Clearwell Measurements
Example
Inside Length
Inside Width
Measure total length of all walls
Measure outside dimensions of support columns and count columns.
Back to Main

## Rectangular Clearwell Worksheet
Rectangular Clearwell Drawdown Meter Accuracy Test
| 0 |  |  |  |  | Date:
Dimensions
|  | Clearwell Length: | ft. |  | in.
|  | Clearwell Width: | ft. |  | in.
|  | Total Baffle Wall Length: | ft. |  | in.
|  | Baffle Wall Thickness: | ft. |  | in.
|  | Support Column Dimensions: | ft. |  | in. | X | ft. | in.
Number of Columns:
Test Results
|  | Clearwell Drop During Test: | in.
Clearwell Gallons Pumped:
Gallons from Master Meter:
|  | Meter Accuracy: |  | %
Back to Main
Back to Main

## 2 Rectangular Clearwells
Rectangular Clearwell Drawdown Meter Accuracy Test
| 0 | [5 empty] | Date:
Clearwell 1 Dimensions
|  | Clearwell Length: |  | ft. |  | in.
|  | Clearwell Width: |  | ft. |  | in.
|  | Total Baffle Wall Length: |  | ft. |  | in.
|  | Baffle Wall Thickness: |  | ft. |  | in.
|  | Support Column Dimensions: |  | ft. |  | in. | X | ft. | in.
Number of Columns:
|  | Clearwell Drop During Test: |  | in.
Clearwell 1 Gallons Pumped:
Clearwell 2 Dimensions
|  | Clearwell Length: |  | ft. |  | in.
|  | Clearwell Width: |  | ft. |  | in.
|  | Total Baffle Wall Length: |  | ft. |  | in.
|  | Baffle Wall Thickness: |  | ft. |  | in.
|  | Support Column Dimensions: |  | ft. |  | in. | X | ft. | in.
Number of Columns:
|  | Clearwell Drop During Test: |  | in.
Clearwell 2 Gallons Pumped:
|  | Total Gallons Pumped: | 0
Gallons from Master Meter:
|  | Meter Accuracy: |  |  | %
Back to Main

## Round Clearwell Example
Round Clearwell Measurements
Example
Measure outside dimensions of support columns and count columns.
Measure total length of all walls
Measure inside diameter of clearwell
Back to Main

## Round Clearwell Worksheet
Round Clearwell Drawdown Meter Accuracy Test
| 0 |  |  |  |  | Date:
Dimensions
|  | Clearwell Diameter: | ft. |  | in.
|  | Total Baffle Wall Length: | ft. |  | in.
|  | Baffle Wall Thickness: | ft. |  | in.
|  | Support Column Dimensions: | ft. |  | in. | X | ft. | in.
Number of Columns:
Test Results
|  | Clearwell Drop During Test: | in.
Clearwell Gallons Pumped:
Gallons from Master Meter:
|  | Meter Accuracy: |  | %
Back to Main